## Instructions
The VFD Survey is provided to facilitate the completion of Final Applications that involve HVAC equipment retrofitted with VFD. Information required to calculate the demand and energy savings for VFD consists of the following:
Measure Description
This measure involves the installation of a variable frequency drive (VFD) on an existing motor in a commericail HVAC application (AHU Supply fan or Chilled/Hot Primary/Secondary Water Pumps) to replace the existing control system. This measure is applicable to both primary and secondary hot or chilled water pumping systems. This measure does not apply to controls installed on the HVAC compressor. This measure accounts for the interactive HVAC demand savings during the summer peak period.
Eligibility Criteria
Supply fans may not have variable pitch. New construction and constant-volume systems are ineligible. Motor HPs must be less than or equal to 100 HP. Equipment used for process loads is ineligible.
Baseline Condition
The AHU Supply fan baselines is a centrifugal supply fan with a single-speed motor on a direct expansion (DX) variable air volume (VAV) or constant air volume (CAV) air handling unit (AHU). The motor is a standard efficiency motor based on ASHRAE Standard 90.1-2004. The AHU has a standard cooling efficiency based on IECC 2015. The HVAC pump baseline is a constant speed pump with standard-efficiency motor.
High-Efficiency Condition
The high efficiency condition is an installation of a VFD on an AHU supply fan, hot water pump, or chilled water pump. The existing damper or inlet guide vane will be removed or set completely open permanently after installation. The VFD will maintain a constant static pressure by adjusting fan speed and delivering the same amount of flow as the baseline condition.
Column 1 VFD count
The number of VFD to be installed.
Column 2 Building Type
Building Type of which the building is where the VFD is to be installed.
Column 3 Motor HP Size
The size of the pump motor, or the size of the AHU supply fan motor.
Column 4 HVAC System
The HVAC System that the VFD will be installed on.
AHU Supply Fan
HVAC Chilled Water Pump
HVAC Hot Water Pump
Column 4 Baseline Part-Load Control Type
Four part-load control types are available for the AHU Supply Fan:
Outlet Damper Part-Load Fan Control
Inlet Damper Part-Load Fan Control
Inlet Guide Vane Part-Load Fan Control
No Fan Control

## HVAC VFD
CenterPoint Energy C&I Standard Offer Program |  |  |  | FOR ESTIMATION PURPOSES ONLY
VFD for Water Pumping Measure
7
Project Name: |  |  |  | Date:
Sponsor Name: |  |  |  | Project #:
Please fill out this form for each site where a VFD measure is being applied.
VFD Characteristics
Construction Type | Retrofit
Climate Zone | Houston
VFD # | Count | Motor Size |  |  | kW Saving | kWh Saving
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
Total Count: | 0 |  |  |  | 0 | 0
Savings Estimate
| VFD kW Savings |  |  | 0
| VFD kWh Savings |  |  | 0
| Cooling System Types |  | Cooling Size Categories
| Chiller with air-cooled condenser |  | 1
| Chiller with water-cooled condenser |  | 2
| DX packaged AC |  | 3
DX window AC
Packaged evaporative cooler
Heat pump
Ammonia
None
Other (please describe)
Note on B15: Enter the VFD quantity in this column.
Note on C15: Enter motor size in hp

## Lookup Values (hidden)
Pump VFD savings per motor HP |  | kWh/hp | kW/hp
| Amarillo | 1389 | 0.097
| Dallas |  | 0.069
| Houston |  | 0.067
| Corpus Christi |  | 0.138
| El Paso |  | 0.106